## Sheet1
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles
"DR" Speed (TCC 175-6-2) | [9 empty] | "DR" Speed (TCC 175-6-2)
Total Clearing Time-Current Characteristic Curves Dated July 17, 2000 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated July 17, 2000
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3DR |  | 4DR |  | 5DR |  | 7DR |  | 10DR |  | 15DR |  | 20DR
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
10000 | 0.013351 | 10000 | 0.013351 | 10000 | 0.013351 | 10000 | 0.013351 | 10000 | 0.013351 | 10000 | 0.013351 | 10000 | 0.013351
5237.775 | 0.013583 | 5237.775 | 0.013583 | 5237.775 | 0.013583 | 5237.775 | 0.013583 | 5237.775 | 0.013583 | 5237.775 | 0.013583 | 5237.775 | 0.013583
3956.9536 | 0.013778 | 3956.9536 | 0.013778 | 3956.9536 | 0.013778 | 3956.9536 | 0.013778 | 3956.9536 | 0.013778 | 3956.9536 | 0.013778 | 3956.9536 | 0.013778
3652.2878 | 0.014057 | 3652.2878 | 0.014057 | 3652.2878 | 0.014057 | 3652.2878 | 0.014057 | 3652.2878 | 0.014057 | 3652.2878 | 0.014057 | 3652.2878 | 0.014057
3165.4054 | 0.014424 | 3165.4054 | 0.014424 | 3165.4054 | 0.014424 | 3165.4054 | 0.014424 | 3165.4054 | 0.014424 | 3165.4054 | 0.014424 | 3165.4054 | 0.014424
2546.7314 | 0.015057 | 2546.7314 | 0.015057 | 2546.7314 | 0.015057 | 2546.7314 | 0.015057 | 2546.7314 | 0.015057 | 2546.7314 | 0.015057 | 2546.7314 | 0.015057
1957.2826 | 0.016266 | 1957.2826 | 0.016266 | 1957.2826 | 0.016266 | 1957.2826 | 0.016266 | 1957.2826 | 0.016266 | 1957.2826 | 0.016266 | 1957.2826 | 0.016266
1625.0891 | 0.017623 | 1625.0891 | 0.017623 | 1625.0891 | 0.017623 | 1625.0891 | 0.017623 | 1625.0891 | 0.017623 | 1625.0891 | 0.017623 | 1625.0891 | 0.017623
1360.9087 | 0.019424 | 1360.9087 | 0.019424 | 1360.9087 | 0.019424 | 1360.9087 | 0.019424 | 1360.9087 | 0.019424 | 1360.9087 | 0.019424 | 1360.9087 | 0.019424
1156.0972 | 0.021594 | 1156.0972 | 0.021594 | 1156.0972 | 0.021594 | 1156.0972 | 0.021594 | 1156.0972 | 0.021594 | 1156.0972 | 0.021594 | 1156.0972 | 0.021594
973.7143 | 0.024703 | 973.7143 | 0.024703 | 973.7143 | 0.024703 | 973.7143 | 0.024703 | 973.7143 | 0.024703 | 973.7143 | 0.024703 | 973.7143 | 0.024703
824.8105 | 0.028748 | 824.8105 | 0.028748 | 824.8105 | 0.028748 | 824.8105 | 0.028748 | 824.8105 | 0.028748 | 824.8105 | 0.028748 | 824.8105 | 0.028748
688.7526 | 0.034824 | 688.7526 | 0.034824 | 688.7526 | 0.034824 | 688.7526 | 0.034824 | 688.7526 | 0.034824 | 688.7526 | 0.034824 | 688.7526 | 0.034824
444.5577 | 0.062614 | 444.5577 | 0.062614 | 444.5577 | 0.062614 | 444.5577 | 0.062614 | 444.5577 | 0.062614 | 444.5577 | 0.062614 | 444.5577 | 0.062614
316.2608 | 0.10816 | 316.2608 | 0.10816 | 316.2608 | 0.10816 | 316.2608 | 0.10816 | 316.2608 | 0.10816 | 316.2608 | 0.10816 | 316.2608 | 0.10816
168.5188 | 0.35468 | 168.5188 | 0.35468 | 168.5188 | 0.35468 | 168.5188 | 0.35468 | 168.5188 | 0.35468 | 168.5188 | 0.35468 | 168.5188 | 0.35468
100.9724 | 1.0859 | 100.9724 | 1.0859 | 100.9724 | 1.0859 | 100.9724 | 1.0859 | 100.9724 | 1.0859 | 100.9724 | 1.0859 | 100.9724 | 1.0859
74.5547 | 2.0265 | 74.5547 | 2.0265 | 87.7627 | 1.5397 | 87.7627 | 1.5397 | 74.5547 | 2.0265 | 87.7627 | 1.5397 | 87.7627 | 1.5397
54.5782 | 4.18 | 54.5782 | 4.18 | 74.3417 | 2.2528 | 75.8458 | 2.4061 | 54.5782 | 4.18 | 74.3417 | 2.2528 | 75.8458 | 2.4061
47.1673 | 5.0635 | 52.2852 | 4.6204 | 61.9012 | 3.5509 | 67.643 | 3.7493 | 52.2852 | 4.6204 | 61.9012 | 3.5509 | 67.643 | 3.7493
29.7553 | 10.092 | 39.3868 | 7.0975 | 54.5782 | 4.9631 | 63.1536 | 5.3311 | 43.0402 | 7.4301 | 54.5782 | 4.9631 | 63.1536 | 5.3311
21.9076 | 16.1826 | 25.3497 | 14.8938 | 49.2359 | 6.8188 | 52.5853 | 7.2204 | 38.3854 | 10.1499 | 49.2359 | 6.8188 | 58.291 | 10.0344
15.946 | 28.0334 | 16.8852 | 31.9777 | 46.7641 | 8.1893 | 40.0688 | 11.9483 | 35.6332 | 13.0567 | 46.7641 | 8.1893 | 55.6825 | 17.8363
13.4304 | 38.9587 | 13.1265 | 54.7651 | 40.0688 | 10.4745 | 31.4178 | 19.3244 | 32.702 | 18.4595 | 44.163 | 10.5648 | 48.815 | 236.3751
11.3117 | 56.1939 | 11.5405 | 74.8126 | 24.0771 | 25.1448 | 24.776 | 32.2534 | 29.5855 | 30.634 | 40.4143 | 20.1143 | 48.2595 | 300.6087
9.3918 | 88.0678 | 10.4407 | 98.7487 | 19.8198 | 37.3217 | 19.8766 | 56.355 | 28.1808 | 41.8481 | 37.4095 | 84.1263
8.3761 | 120.3063 | 9.2584 | 155.2038 | 15.2324 | 68.6577 | 17.1776 | 88.8272 | 25.5682 | 100.7468 | 35.9404 | 259.7861
7.5996 | 172.5392 | 8.5212 | 254.6338 | 13.2018 | 105.7694 | 15.5852 | 135.6714 | 24.2152 | 247.45 | 35.7353 | 300.6087
7.0749 | 256.8293 | 8.4242 | 300.6087 | 11.7068 | 183.7514 | 14.4264 | 241.1581 | 24.0771 | 300.6087
6.9545 | 300.6087 |  |  | 11.151 | 257.5653 | 14.1808 | 300.6087
|  |  |  | 10.9299 | 300.6087