## Parallel Minimum Melt
S&C Parallel Fault Fiter Electronic Power Fuses | [9 empty] | S&C Parallel Fault Fiter Electronic Power Fuses
Inverse Curve-Type Control Modules (TCC 410-7-P) | [9 empty] | Inverse Curve-Type Control Modules (TCC 410-7-P)
Minimum Melting Time-Current Characteristic Curves dated June 12, 2017 | [9 empty] | Minimum Melting Time-Current Characteristic Curves dated June 12, 2017
Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10%
2x400A |  | 2x500A |  | 2x600A |  | 2x700A |  | 2x800A |  | 2x1000A |  | 2x1250A |  | 2x1500A
Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s)
720 | 700 | 900 | 700 | 1080 | 700 | 1260 | 700 | 1440 | 700 | 1800 | 700 | 2250 | 700 | 2700 | 700
720 | 500 | 900 | 500 | 1080 | 500 | 1260 | 500 | 1440 | 500 | 1800 | 500 | 2250 | 500 | 2700 | 500
720 | 300 | 900 | 300 | 1080 | 300 | 1260 | 300 | 1440 | 300 | 1800 | 300 | 2250 | 300 | 2700 | 300
720 | 200 | 900 | 200 | 1080 | 200 | 1260 | 200 | 1440 | 200 | 1800 | 200 | 2250 | 200 | 2700 | 200
720 | 100 | 900 | 100 | 1080 | 100 | 1260 | 100 | 1440 | 100 | 1800 | 100 | 2250 | 100 | 2700 | 100
729 | 70 | 909 | 70 | 1084.5 | 70 | 1269 | 70 | 1449 | 70 | 1809 | 70 | 2268 | 70 | 2718 | 70
738 | 50 | 913.5 | 50 | 1089 | 50 | 1278 | 50 | 1458 | 50 | 1818 | 50 | 2286 | 50 | 2727 | 50
742.5 | 30 | 918 | 30 | 1098 | 30 | 1287 | 30 | 1467 | 30 | 1836 | 30 | 2313 | 30 | 2736 | 30
747 | 20 | 936 | 20 | 1107 | 20 | 1296 | 20 | 1476 | 20 | 1881 | 20 | 2340 | 20 | 2799 | 20
783 | 10 | 990 | 10 | 1197 | 10 | 1386 | 10 | 1575 | 10 | 1980 | 10 | 2511 | 10 | 2916 | 10
819 | 7 | 1044 | 7 | 1269 | 7 | 1449 | 7 | 1638 | 7 | 2124 | 7 | 2610 | 7 | 3078 | 7
864 | 5 | 1107 | 5 | 1341 | 5 | 1530 | 5 | 1773 | 5 | 2223 | 5 | 2817 | 5 | 3258 | 5
990 | 3 | 1260 | 3 | 1512 | 3 | 1746 | 3 | 1980 | 3 | 2520 | 3 | 3204 | 3 | 3744 | 3
1134 | 2 | 1404 | 2 | 1728 | 2 | 1989 | 2 | 2313 | 2 | 2880 | 2 | 3600 | 2 | 4140 | 2
1494 | 1 | 1890 | 1 | 2340 | 1 | 2700 | 1 | 3096 | 1 | 3870 | 1 | 4842 | 1 | 5715 | 1
1809 | 0.7 | 2304 | 0.7 | 2862 | 0.7 | 3294 | 0.7 | 3825 | 0.7 | 4752 | 0.7 | 5904 | 0.7 | 6930 | 0.7
2250 | 0.5 | 2880 | 0.5 | 3582 | 0.5 | 4104 | 0.5 | 4815 | 0.5 | 5940 | 0.5 | 7560 | 0.5 | 8730 | 0.5
3267 | 0.3 | 4230 | 0.3 | 5175 | 0.3 | 6030 | 0.3 | 7200 | 0.3 | 8910 | 0.3 | 11340 | 0.3 | 13995 | 0.3
4500 | 0.2 | 5976 | 0.2 | 7470 | 0.2 | 8730 | 0.2 | 10440 | 0.2 | 12960 | 0.2 | 16740 | 0.2 | 21330 | 0.2
8910 | 0.1 | 12240 | 0.1 | 14940 | 0.1 | 18000 | 0.1 | 21600 | 0.1 | 26460 | 0.1 | 34560 | 0.1 | 40000 | 0.10746
13680 | 0.07 | 19080 | 0.07 | 22680 | 0.07 | 27000 | 0.07 | 33840 | 0.07 | 39600 | 0.07 | 40000 | 0.088568
20700 | 0.05 | 28980 | 0.05 | 34200 | 0.05 | 40000 | 0.051042 | 40000 | 0.060661 | 40000 | 0.069419
40000 | 0.030863 | 40000 | 0.039553 | 40000 | 0.044343
2x400A |  | 2x500A |  | 2x600A |  | 2x700A |  | 2x800A |  | 2x1000A |  | 2x1250A |  | 2x1500A
Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s) | Current (A) | Time (s)
72000 | 0.0211 | 72000 | 0.026 | 72000 | 0.028 | 72000 | 0.032 | 72000 | 0.0375 | 72000 | 0.043 | 72000 | 0.0545 | 72000 | 0.063
41580 | 0.03 | 58500 | 0.03 | 66600 | 0.03 | 41040 | 0.05 | 50130 | 0.05 | 67500 | 0.045 | 53100 | 0.07 | 63000 | 0.07
20700 | 0.05 | 28980 | 0.05 | 34200 | 0.05 | 27000 | 0.07 | 33840 | 0.07 | 59400 | 0.05 | 34560 | 0.1 | 43020 | 0.1
13680 | 0.07 | 19080 | 0.07 | 22680 | 0.07 | 18000 | 0.1 | 21600 | 0.1 | 39600 | 0.07 | 16740 | 0.2 | 21330 | 0.2
8910 | 0.1 | 12240 | 0.1 | 14940 | 0.1 | 8730 | 0.2 | 10440 | 0.2 | 26460 | 0.1 | 11340 | 0.3 | 13995 | 0.3
4500 | 0.2 | 5976 | 0.2 | 7470 | 0.2 | 6030 | 0.3 | 7200 | 0.3 | 12960 | 0.2 | 7560 | 0.5 | 8730 | 0.5
3267 | 0.3 | 4230 | 0.3 | 5175 | 0.3 | 4104 | 0.5 | 4815 | 0.5 | 8910 | 0.3 | 5904 | 0.7 | 6930 | 0.7
2250 | 0.5 | 2880 | 0.5 | 3582 | 0.5 | 3294 | 0.7 | 3825 | 0.7 | 5940 | 0.5 | 4842 | 1 | 5715 | 1
1809 | 0.7 | 2304 | 0.7 | 2862 | 0.7 | 2700 | 1 | 3096 | 1 | 4752 | 0.7 | 3600 | 2 | 4140 | 2
1494 | 1 | 1890 | 1 | 2340 | 1 | 1989 | 2 | 2313 | 2 | 3870 | 1 | 3204 | 3 | 3744 | 3
1134 | 2 | 1404 | 2 | 1728 | 2 | 1746 | 3 | 1980 | 3 | 2880 | 2 | 2817 | 5 | 3258 | 5
990 | 3 | 1260 | 3 | 1512 | 3 | 1530 | 5 | 1773 | 5 | 2520 | 3 | 2610 | 7 | 3078 | 7
864 | 5 | 1107 | 5 | 1341 | 5 | 1449 | 7 | 1638 | 7 | 2223 | 5 | 2511 | 10 | 2916 | 10
819 | 7 | 1044 | 7 | 1269 | 7 | 1386 | 10 | 1575 | 10 | 2124 | 7 | 2340 | 20 | 2799 | 20
783 | 10 | 990 | 10 | 1197 | 10 | 1296 | 20 | 1476 | 20 | 1980 | 10 | 2313 | 30 | 2736 | 30
747 | 20 | 936 | 20 | 1107 | 20 | 1287 | 30 | 1467 | 30 | 1881 | 20 | 2286 | 50 | 2727 | 50
742.5 | 30 | 918 | 30 | 1098 | 30 | 1278 | 50 | 1458 | 50 | 1836 | 30 | 2268 | 70 | 2718 | 70
738 | 50 | 913.5 | 50 | 1089 | 50 | 1269 | 70 | 1449 | 70 | 1818 | 50 | 2250 | 100 | 2700 | 100
729 | 70 | 909 | 70 | 1084.5 | 70 | 1260 | 100 | 1440 | 100 | 1809 | 70 | 2250 | 200 | 2700 | 200
720 | 100 | 900 | 100 | 1080 | 100 | 1260 | 200 | 1440 | 200 | 1800 | 100 | 2250 | 300 | 2700 | 300
720 | 200 | 900 | 200 | 1080 | 200 | 1260 | 300 | 1440 | 300 | 1800 | 200 | 2250 | 500 | 2700 | 500
720 | 300 | 900 | 300 | 1080 | 300 | 1260 | 500 | 1440 | 500 | 1800 | 300 | 2250 | 700 | 2700 | 700
720 | 500 | 900 | 500 | 1080 | 500 | 1260 | 700 | 1440 | 700 | 1800 | 500
720 | 700 | 900 | 700 | 1080 | 700 |  |  |  |  | 1800 | 700