## 153_152
S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV)
Standard Speed (TCC 153-1-5-2) | [9 empty] | Standard Speed (TCC 153-1-5-2) | [9 empty] | Standard Speed (TCC 153-1-5-2) | [9 empty] | Standard Speed (TCC 153-1-5-2) | [9 empty] | Standard Speed (TCC 153-1-5-2)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E |  | 2-300E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
42998.7 | 0.016307 | 42998.7 | 0.016307 | 42998.7 | 0.016307 | 33454 | 0.018608 | 42998.7 | 0.016703 | 42998.7 | 0.016307 | 42998.7 | 0.016307 | 42998.7 | 0.016307 | 42998.7 | 0.016307 | 42998.7 | 0.016307 | 38251 | 0.017489 | 42998.7 | 0.016405 | 42998.7 | 0.016405 | 42998.7 | 0.016504 | 42366.7 | 0.01598 | 42342.4 | 0.027747 | 42366.7 | 0.02781 | 42366.7 | 0.027922 | 42366.7 | 0.028668 | 42366.7 | 0.029282 | 42342.4 | 0.030047 | 42391 | 0.031583 | 42366.7 | 0.033599
40657 | 0.016703 | 40657 | 0.016703 | 40779.1 | 0.016703 | 32013.9 | 0.018608 | 40779.1 | 0.016703 | 40860.8 | 0.016703 | 41189 | 0.016603 | 41478.3 | 0.016603 | 40212.2 | 0.016803 | 40657 | 0.016803 | 36824.7 | 0.017489 | 40616.3 | 0.016803 | 41561.3 | 0.016703 | 41189 | 0.016803 | 38523.1 | 0.016719 | 35048.3 | 0.029858 | 34451 | 0.030047 | 34352.5 | 0.030254 | 37801.6 | 0.02991 | 38479 | 0.030446 | 38700.1 | 0.031313 | 36357.2 | 0.034418 | 37693.5 | 0.036073
39101.9 | 0.016989 | 39180.1 | 0.016989 | 39297.9 | 0.016989 | 30574.6 | 0.019003 | 39337.2 | 0.016989 | 39455.4 | 0.016989 | 39732.5 | 0.016888 | 40051.7 | 0.016888 | 38790.3 | 0.017092 | 39258.6 | 0.016989 | 35416.2 | 0.017896 | 39180.1 | 0.017092 | 40131.8 | 0.016989 | 39732.5 | 0.017092 | 31469.4 | 0.018707 | 26560.7 | 0.033484 | 28614.5 | 0.032464 | 25385.3 | 0.034359 | 31686.5 | 0.032315 | 32439.7 | 0.03314 | 31469.4 | 0.035095 | 29027.3 | 0.039469 | 32794.7 | 0.039855
37531.1 | 0.017402 | 37681.5 | 0.017298 | 37794.7 | 0.017298 | 29170.9 | 0.019406 | 37908.3 | 0.017298 | 38022.2 | 0.017298 | 38327.6 | 0.017194 | 38635.4 | 0.017092 | 37343.9 | 0.017402 | 37832.6 | 0.017298 | 33993.5 | 0.018203 | 37757 | 0.017402 | 38674.1 | 0.017194 | 38327.6 | 0.017402 | 25341.7 | 0.02093 | 18187.4 | 0.039244 | 20418.9 | 0.037507 | 19359.4 | 0.03893 | 25502 | 0.035601 | 26273.1 | 0.037016 | 26606.4 | 0.038841 | 22353.5 | 0.046899 | 27886.2 | 0.045132
35987.4 | 0.0177 | 36167.8 | 0.017594 | 36312.8 | 0.017594 | 27720.4 | 0.019798 | 36458.3 | 0.017594 | 36567.9 | 0.017594 | 36898.5 | 0.017489 | 37194.8 | 0.017402 | 35915.5 | 0.0177 | 36385.5 | 0.017594 | 32562.8 | 0.018608 | 36349.1 | 0.0177 | 37269.3 | 0.017594 | 36898.5 | 0.0177 | 19762.9 | 0.023539 | 12779.1 | 0.046047 | 14908.4 | 0.043482 | 14273.2 | 0.045366 | 20036.5 | 0.039993 | 20642.4 | 0.042133 | 22073.5 | 0.043908 | 18250.1 | 0.054935 | 23563.3 | 0.052173
34403.9 | 0.018004 | 34680.2 | 0.018004 | 34819.2 | 0.018004 | 26289.5 | 0.020299 | 35028.8 | 0.017896 | 35134 | 0.017896 | 35451.7 | 0.017789 | 35772.2 | 0.0177 | 34507.3 | 0.018004 | 34958.8 | 0.018004 | 31129.9 | 0.018908 | 34923.9 | 0.018004 | 35808 | 0.017896 | 35451.7 | 0.018004 | 14917 | 0.027087 | 9745.68 | 0.052775 | 11304.6 | 0.050036 | 10559.5 | 0.053628 | 15403.3 | 0.045968 | 16718.4 | 0.047822 | 18386.5 | 0.049722 | 14942.7 | 0.066218 | 20302.3 | 0.060071
32857.2 | 0.018404 | 33187.4 | 0.018294 | 33320.4 | 0.018294 | 24857.8 | 0.020792 | 33621.6 | 0.018203 | 33722.7 | 0.018203 | 34027.5 | 0.018094 | 34335.2 | 0.018094 | 33054.9 | 0.018404 | 33520.9 | 0.018294 | 29700.7 | 0.019309 | 33487.4 | 0.018404 | 34403.9 | 0.018203 | 34027.5 | 0.018404 | 10179.4 | 0.033426 | 7339.2 | 0.062173 | 8948.26 | 0.057314 | 8206.68 | 0.06307 | 11814.4 | 0.05406 | 13241.2 | 0.055855 | 14322.4 | 0.060417 | 11699.9 | 0.087432 | 17086.4 | 0.072534
31286 | 0.018795 | 31695.4 | 0.018701 | 31822.4 | 0.018701 | 23433.6 | 0.021297 | 32174.4 | 0.018608 | 32271 | 0.018608 | 32595.4 | 0.018497 | 32923 | 0.018404 | 31632 | 0.018795 | 32110.1 | 0.018608 | 28252.2 | 0.019699 | 32045.9 | 0.018701 | 32955.9 | 0.018608 | 32595.4 | 0.018795 | 8034.55 | 0.038796 | 5995.38 | 0.070972 | 7284.74 | 0.065388 | 6323.48 | 0.077032 | 9072.15 | 0.065126 | 10991.6 | 0.064458 | 11679.8 | 0.07316 | 9790.45 | 0.10983 | 14612.5 | 0.087833
29730.4 | 0.019213 | 30209.9 | 0.019098 | 30331 | 0.019098 | 22002.8 | 0.021815 | 30758.6 | 0.019003 | 30851 | 0.018908 | 31161.1 | 0.018908 | 31474.3 | 0.018795 | 30209.9 | 0.019098 | 30666.5 | 0.019003 | 26820.6 | 0.020198 | 30605.2 | 0.019098 | 31537.3 | 0.018908 | 31161.1 | 0.019213 | 6173.14 | 0.046418 | 4833.5 | 0.084332 | 6251.44 | 0.073118 | 4794.88 | 0.10015 | 7509.33 | 0.076285 | 8725.51 | 0.079635 | 9261.21 | 0.094843 | 8192.59 | 0.14067 | 12347.3 | 0.10951
28167.5 | 0.019699 | 28707.8 | 0.019503 | 28822.9 | 0.019503 | 20576.9 | 0.022502 | 29317.1 | 0.019406 | 29434.6 | 0.019309 | 29730.4 | 0.019309 | 30059.2 | 0.019213 | 28765.3 | 0.019503 | 29229.3 | 0.019406 | 25410.7 | 0.020689 | 29200 | 0.019503 | 30119.4 | 0.019309 | 29730.4 | 0.019582 | 4667.49 | 0.058241 | 3883.42 | 0.10377 | 5100.94 | 0.087132 | 3839.17 | 0.12857 | 5944.07 | 0.096709 | 7330.79 | 0.096267 | 8016.16 | 0.11393 | 6847.65 | 0.18564 | 10439.2 | 0.13891
26606.9 | 0.020198 | 27198.7 | 0.019997 | 27335.1 | 0.019897 | 19147.5 | 0.023094 | 27887.3 | 0.019798 | 27999 | 0.019798 | 28308.7 | 0.019699 | 28621.8 | 0.019582 | 27362.4 | 0.019997 | 27803.7 | 0.019897 | 23978.8 | 0.021191 | 27748.2 | 0.019997 | 28679.1 | 0.019798 | 28308.7 | 0.019997 | 3707.32 | 0.073665 | 3392.29 | 0.11989 | 4241.62 | 0.10461 | 3045.9 | 0.1746 | 4640.83 | 0.12983 | 6215.73 | 0.11758 | 6616.26 | 0.14812 | 5736.64 | 0.25007 | 8948.26 | 0.1754
25057.4 | 0.020689 | 25717.5 | 0.020503 | 25846.4 | 0.020401 | 17710.7 | 0.023798 | 26474.2 | 0.020198 | 26553.7 | 0.020198 | 26874.3 | 0.020097 | 27198.7 | 0.019997 | 25924 | 0.020401 | 26368.5 | 0.020299 | 22537.3 | 0.021815 | 26315.8 | 0.020401 | 27253.2 | 0.020198 | 26874.3 | 0.020503 | 3004.31 | 0.093924 | 2785.48 | 0.15077 | 3535.15 | 0.12784 | 2301.68 | 0.26452 | 3930.42 | 0.1616 | 5423.42 | 0.14051 | 5655.06 | 0.18564 | 4734.83 | 0.34866 | 7197.62 | 0.24993
23504 | 0.021297 | 24219.8 | 0.021001 | 24341.2 | 0.020897 | 16283.8 | 0.024596 | 25032.4 | 0.020689 | 25132.7 | 0.020689 | 25436.1 | 0.020606 | 25768.9 | 0.020503 | 24487.7 | 0.020897 | 24957.4 | 0.020792 | 21097.8 | 0.022412 | 24907.5 | 0.020897 | 25820.5 | 0.020689 | 25436.1 | 0.021001 | 2471.14 | 0.12141 | 2288.53 | 0.19614 | 2973.48 | 0.1593 | 1831.33 | 0.38148 | 3482.88 | 0.19224 | 4616.96 | 0.176 | 4968.26 | 0.22778 | 4193.29 | 0.43323 | 6219.29 | 0.32252
21936.9 | 0.021902 | 22718.3 | 0.021598 | 22855 | 0.021511 | 14852.5 | 0.025498 | 23598.2 | 0.021191 | 23716.5 | 0.021191 | 24026.8 | 0.021107 | 24341.2 | 0.021001 | 23061.6 | 0.021511 | 23504 | 0.021297 | 19671.5 | 0.022979 | 23457 | 0.021511 | 24389.9 | 0.021297 | 24002.8 | 0.021598 | 2024.46 | 0.16142 | 1908.45 | 0.25602 | 2476.81 | 0.20604 | 1517.59 | 0.53249 | 3044.16 | 0.23534 | 4084.22 | 0.21398 | 4285.59 | 0.29008 | 3565.66 | 0.58328 | 5435.87 | 0.4084
20372.2 | 0.022502 | 21224.8 | 0.022211 | 21352.5 | 0.0221 | 13425.7 | 0.026485 | 22179.5 | 0.021815 | 22268.4 | 0.021706 | 22582.4 | 0.021598 | 22900.8 | 0.021511 | 21631.9 | 0.0221 | 22091 | 0.021902 | 18250.1 | 0.023703 | 22046.9 | 0.0221 | 22946.6 | 0.021815 | 22582.4 | 0.022211 | 1581.5 | 0.23914 | 1615.39 | 0.33342 | 2041.94 | 0.27377 | 1268.46 | 0.74454 | 2665.27 | 0.29075 | 3569.75 | 0.26619 | 3713.69 | 0.3722 | 3121.87 | 0.75962 | 4737.54 | 0.52551
18805.9 | 0.023303 | 19730.6 | 0.022796 | 19869.2 | 0.022796 | 12003.1 | 0.027594 | 20742.2 | 0.022412 | 20846.2 | 0.0223 | 21161.2 | 0.022211 | 21481 | 0.0221 | 20189.6 | 0.022705 | 20659.4 | 0.022502 | 16813.3 | 0.024498 | 20597.5 | 0.022705 | 21524 | 0.022412 | 21161.2 | 0.022887 | 1243.99 | 0.36024 | 1376.75 | 0.43622 | 1702.81 | 0.36754 | 1062.65 | 1.0561 | 2254.69 | 0.38389 | 3109.38 | 0.33611 | 3262.67 | 0.46593 | 2688.28 | 1.0339 | 4183.69 | 0.6735
17256.2 | 0.024109 | 18231.8 | 0.023584 | 18378.3 | 0.02349 | 10571.6 | 0.028893 | 19320.6 | 0.022979 | 19417.4 | 0.022979 | 19730.6 | 0.022887 | 20048.8 | 0.022705 | 18768.3 | 0.023397 | 19224.2 | 0.023187 | 15381.6 | 0.025396 | 19185.8 | 0.023397 | 20088.9 | 0.023094 | 19730.6 | 0.023584 | 986.386 | 0.54577 | 1187.58 | 0.56876 | 1478.97 | 0.46996 | 929.33 | 1.3992 | 1877.01 | 0.52884 | 2679.05 | 0.43448 | 2846.79 | 0.59852 | 2372.64 | 1.3644 | 3758.65 | 0.83543
15692.3 | 0.024993 | 16746.2 | 0.0244 | 16880.7 | 0.024303 | 9135.54 | 0.030404 | 17888.7 | 0.023798 | 17978.4 | 0.023703 | 18304.9 | 0.023584 | 18618.8 | 0.023397 | 17342.7 | 0.024109 | 17799.5 | 0.023893 | 13959.6 | 0.026406 | 17746.2 | 0.024206 | 18656 | 0.023893 | 18286.6 | 0.0244 | 831.572 | 0.74925 | 960.179 | 0.84506 | 1322.63 | 0.574 | 826.821 | 1.8379 | 1615.39 | 0.69666 | 2379.45 | 0.53862 | 2450 | 0.8035 | 2060.74 | 1.9154 | 3315.44 | 1.0942
14128.1 | 0.026013 | 15243.7 | 0.025295 | 15381.6 | 0.025194 | 7707.34 | 0.032285 | 16447.4 | 0.024498 | 16563 | 0.024498 | 16863.8 | 0.024303 | 17187.3 | 0.024206 | 15913.5 | 0.024893 | 16365.4 | 0.024695 | 12530.5 | 0.027594 | 16316.4 | 0.024993 | 17238.9 | 0.024695 | 16863.8 | 0.025295 | 705.892 | 1.0245 | 810.406 | 1.1782 | 1131.13 | 0.77058 | 729.742 | 2.5802 | 1409.48 | 0.91041 | 2124.27 | 0.66659 | 2146.29 | 1.0464 | 1864.15 | 2.5464 | 2963.28 | 1.4137
12580.8 | 0.027101 | 13751.8 | 0.0263 | 13890 | 0.026222 | 6278.76 | 0.034522 | 15016.8 | 0.025396 | 15122.3 | 0.025396 | 15443.2 | 0.025194 | 15755.2 | 0.024993 | 14485.8 | 0.025909 | 14941.9 | 0.0256 | 11102.5 | 0.028893 | 14882.2 | 0.026013 | 15802.5 | 0.025702 | 15427.8 | 0.026406 | 603.687 | 1.421 | 704.68 | 1.589 | 942.197 | 1.1069 | 654.852 | 3.7318 | 1255.44 | 1.1688 | 1928.24 | 0.80719 | 1928.24 | 1.322 | 1714.56 | 3.3912 | 2669.86 | 1.8538
11014 | 0.028491 | 12257.9 | 0.027401 | 12393.5 | 0.027292 | 4846.09 | 0.037397 | 13587.8 | 0.026406 | 13696.9 | 0.0263 | 14001.6 | 0.026117 | 14327.3 | 0.026013 | 13055 | 0.026886 | 13506.5 | 0.026698 | 9671.4 | 0.030526 | 13452.6 | 0.027101 | 14370.4 | 0.026698 | 14001.6 | 0.027594 | 535.561 | 1.8666 | 609.595 | 2.2929 | 849.874 | 1.3833 | 613.097 | 5.0042 | 1094.79 | 1.6092 | 1718.49 | 1.0198 | 1669.97 | 1.8645 | 1585.13 | 4.6503 | 2465.49 | 2.3434
9451.49 | 0.030012 | 10763.6 | 0.028691 | 10893.5 | 0.028605 | 3418.4 | 0.041496 | 12160.2 | 0.027484 | 12270.1 | 0.027401 | 12580.8 | 0.027183 | 12899.2 | 0.026993 | 11613.5 | 0.028095 | 12075.4 | 0.027788 | 8241.42 | 0.032382 | 12027.2 | 0.028406 | 12938 | 0.028011 | 12568.2 | 0.029008 | 468.367 | 2.6416 | 543.598 | 3.2393 | 721.015 | 2.0272 | 574.334 | 7.1429 | 980.751 | 2.1504 | 1568.87 | 1.2413 | 1454.6 | 2.7639 | 1484.91 | 6.5508 | 2255.98 | 3.0189
7894.55 | 0.031899 | 9273.61 | 0.030313 | 9404.35 | 0.030102 | 1988.09 | 0.048067 | 10731.3 | 0.028806 | 10839.2 | 0.028691 | 11147 | 0.028491 | 11463.5 | 0.028207 | 10187.6 | 0.029506 | 10645.8 | 0.029212 | 6808.51 | 0.034904 | 10592.7 | 0.029922 | 11509.5 | 0.029506 | 11147 | 0.030679 | 416.227 | 3.7662 | 499.12 | 4.5947 | 641.852 | 2.7909 | 550.809 | 9.5017 | 876.578 | 3.0589 | 1415.14 | 1.5926 | 1326.43 | 3.7532 | 1416.76 | 8.7793 | 2101.27 | 3.7965
6335.53 | 0.034315 | 7777.02 | 0.032091 | 7902.45 | 0.031995 | 558.319 | 0.070781 | 9301.47 | 0.030313 | 9404.35 | 0.030223 | 9719.87 | 0.029922 | 10035.9 | 0.029594 | 8759.8 | 0.031174 | 9218.13 | 0.030771 | 5377.23 | 0.038305 | 9162.99 | 0.031804 | 10086.2 | 0.031299 | 9710.16 | 0.032904 | 379.769 | 5.3023 | 456.184 | 7.3505 | 575.982 | 4.0714 | 530.674 | 12.9771 | 816.933 | 4.0995 | 1291.93 | 2.0295 | 1222.09 | 5.0735 | 1359.51 | 11.7861 | 1980.86 | 4.6476
4773.94 | 0.037397 | 6278.76 | 0.034418 | 6412.01 | 0.034212 | 545.079 | 0.071421 | 7870.9 | 0.032091 | 7973.89 | 0.031899 | 8291.02 | 0.031582 | 8612.14 | 0.031299 | 7331.45 | 0.033201 | 7784.8 | 0.032805 | 3947.86 | 0.04358 | 7738.23 | 0.03411 | 8655.31 | 0.033501 | 8282.73 | 0.03568 | 344.328 | 9.3558 | 428.813 | 11.5985 | 530.37 | 5.9122 | 514.802 | 17.7339 | 763.967 | 5.5861 | 1162 | 2.734 | 1148.76 | 6.9411 | 1310.56 | 16.3481 | 1853.5 | 6.0945
3216.11 | 0.041871 | 4783.5 | 0.037509 | 4914.42 | 0.03721 | 526.858 | 0.0725 | 6444.15 | 0.034315 | 6548.09 | 0.03411 | 6856.33 | 0.033703 | 7179.09 | 0.033401 | 5901.3 | 0.035787 | 6354.56 | 0.035325 | 2517.26 | 0.05474 | 6303.93 | 0.037397 | 7222.3 | 0.036474 | 6849.48 | 0.039709 | 327.21 | 16.1618 | 407.73 | 18.4703 | 492.304 | 9.2281 | 501.412 | 25.7519 | 721.842 | 7.6076 | 1049.94 | 3.7489 | 1092.28 | 9.8623 | 1269.91 | 24.584 | 1772.49 | 7.5771
1655.61 | 0.049382 | 3287.65 | 0.041662 | 3418.4 | 0.041371 | 508.737 | 0.073743 | 5013.69 | 0.037099 | 5114.98 | 0.036877 | 5425.84 | 0.036474 | 5749.85 | 0.036002 | 4469.04 | 0.039511 | 4924.25 | 0.038923 | 2487.24 | 0.055124 | 4875.26 | 0.042165 | 5796.03 | 0.041001 | 5420.42 | 0.045998 | 317.424 | 26.7291 | 394.178 | 27.3489 | 466.759 | 13.9567 | 491.458 | 37.9781 | 688.714 | 10.408 | 962.934 | 5.1437 | 1056.58 | 13.4233 | 1237.59 | 37.438 | 1702.81 | 9.8116
95.1004 | 0.082648 | 1793.51 | 0.048793 | 1925.47 | 0.048163 | 491.239 | 0.074933 | 3582.9 | 0.041124 | 3688.33 | 0.040837 | 3999.51 | 0.040229 | 4319.64 | 0.039709 | 3037.92 | 0.045313 | 3494.44 | 0.044415 | 2428.25 | 0.055901 | 3445.86 | 0.05109 | 4363.06 | 0.048356 | 5339.72 | 0.046599 | 308.637 | 48.7567 | 385.247 | 40.2871 | 444.065 | 24.5558 | 485.303 | 53.8377 | 660.504 | 14.6197 | 909.837 | 6.7373 | 1026.16 | 18.6939 | 1222.79 | 50.549 | 1634.94 | 13.4464
92.9381 | 0.083228 | 299.146 | 0.076141 | 430.063 | 0.073229 | 452.565 | 0.077757 | 2151.52 | 0.047636 | 2257.31 | 0.047304 | 2568.12 | 0.046413 | 2889.76 | 0.045722 | 1608.29 | 0.059715 | 2065.09 | 0.05686 | 2351.78 | 0.05686 | 3397.95 | 0.051603 | 4306.7 | 0.048891 | 5202.68 | 0.047398 | 303.551 | 86.0794 | 376.951 | 64.0457 | 430.043 | 42.0562 | 481.978 | 81.146 | 636.36 | 23.0822 | 862.134 | 8.9111 | 1006.94 | 26.8058 | 1214.41 | 67.4352 | 1583.32 | 17.9486
89.0265 | 0.084318 | 294.398 | 0.076676 | 420.284 | 0.073965 | 418.188 | 0.081174 | 721.932 | 0.068278 | 826.278 | 0.066859 | 1137.89 | 0.063535 | 1458.16 | 0.0608 | 1579.6 | 0.060315 | 2034.34 | 0.057374 | 2266.35 | 0.058299 | 3277.8 | 0.052699 | 4179.42 | 0.049779 | 5028.76 | 0.048598 | 299.921 | 144.498 | 370.74 | 106.836 | 423.685 | 71.5351 | 479.773 | 110.004 | 618.035 | 36.3389 | 828.243 | 11.9493 | 985.256 | 38.5703 | 1205.4 | 97.8685 | 1549.22 | 23.122
83.9259 | 0.085935 | 284.556 | 0.077679 | 403.401 | 0.075158 | 386.036 | 0.08491 | 711.895 | 0.068689 | 813.976 | 0.067396 | 1110.9 | 0.064302 | 1425 | 0.061534 | 1535.99 | 0.061227 | 1978.17 | 0.058299 | 2181.85 | 0.059715 | 3161.9 | 0.054033 | 3896.87 | 0.052279 | 4788.29 | 0.050279 | 298.037 | 255.842 | 365.258 | 184.026 | 421.748 | 107.265 | 479.499 | 161.211 | 609.595 | 55.1491 | 798.424 | 16.7751 | 975.148 | 55.6252 | 1200.57 | 140.659 | 1514.12 | 32.2559
79.4346 | 0.087583 | 275.044 | 0.078696 | 381.431 | 0.076906 | 351.402 | 0.08998 | 685.351 | 0.069797 | 787.553 | 0.068415 | 1075.91 | 0.065274 | 1344.7 | 0.063408 | 1477.24 | 0.062526 | 1896.81 | 0.059715 | 2081.67 | 0.061534 | 3037.92 | 0.055345 | 3582.9 | 0.055623 | 4554.76 | 0.052226 | 296.844 | 430.214 | 362.755 | 278.486 | 420.782 | 173.182 | 478.95 | 224.637 | 603.687 | 86.3264 | 772.329 | 23.8759 | 970.689 | 83.1702 | 1202.64 | 199.055 | 1491.73 | 43.3779
74.2126 | 0.089711 | 263.204 | 0.080205 | 360.298 | 0.078853 | 317.962 | 0.096312 | 665.096 | 0.070923 | 755.917 | 0.069797 | 1042.03 | 0.066393 | 1266.39 | 0.065667 | 1405.19 | 0.064302 | 1813.34 | 0.061411 | 1958.49 | 0.064109 | 2924.64 | 0.05686 | 3327.34 | 0.058709 | 4166.9 | 0.055957 | 297.525 | 559 | 358.828 | 441.199 | 420.06 | 263.429 | 481.15 | 333.574 | 600.926 | 120.083 | 756.129 | 33.9242 | 967.358 | 116.358 | 1207.47 | 274.21 | 1471.36 | 60.8614
68.7127 | 0.092721 | 247.629 | 0.082318 | 336.276 | 0.08158 | 289.146 | 0.1035 | 641.578 | 0.071994 | 719.769 | 0.071635 | 998.177 | 0.06787 | 1158.55 | 0.069102 | 1316.76 | 0.066792 | 1714.59 | 0.063535 | 1853.68 | 0.066459 | 2710.61 | 0.059895 | 3065.38 | 0.062714 | 3889.08 | 0.05918 | 298.379 | 601.196 | 357.597 | 599.476 | 420.782 | 401.626 | 481.15 | 450.653 | 597.835 | 182.452 | 746.659 | 48.3672 | 967.912 | 171.995 | 1200.57 | 404.166 | 1460.44 | 82.9323
64.1314 | 0.095736 | 235.316 | 0.084233 | 299.146 | 0.086972 | 263.995 | 0.11156 | 612.734 | 0.073743 | 674.473 | 0.074113 | 944.76 | 0.070007 | 1078.07 | 0.072428 | 1232.66 | 0.069727 | 1598.67 | 0.066459 | 1733.55 | 0.070007 | 2524.83 | 0.063218 | 2795.95 | 0.06787 | 3586.49 | 0.063598 | 298.379 | 601.196 | 357.597 | 599.476 | 421.989 | 564.795 | 481.426 | 559.32 | 597.493 | 269.537 | 737.729 | 69.794 | 969.577 | 251.626 | 1197.83 | 517.981 | 1448.77 | 125.141
59.26 | 0.099444 | 219.408 | 0.087146 | 268.522 | 0.092721 | 240.791 | 0.12122 | 580.524 | 0.075761 | 616.422 | 0.077913 | 895.096 | 0.072283 | 987.257 | 0.076599 | 1145.88 | 0.073156 | 1427.85 | 0.071779 | 1645.71 | 0.072937 | 2337.71 | 0.06706 | 2601.72 | 0.072283 | 3337.34 | 0.06787 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 598.521 | 398.874 | 733.515 | 105.015 | 966.25 | 369.605 | 1197.83 | 517.981 | 1444.63 | 177.705
53.6206 | 0.10507 | 205.189 | 0.09016 | 237.444 | 0.10085 | 219.847 | 0.1325 | 549.457 | 0.078069 | 573.026 | 0.081499 | 842.127 | 0.074933 | 912.265 | 0.081174 | 1058.84 | 0.077292 | 1303.65 | 0.076983 | 1532.92 | 0.077138 | 2106.81 | 0.073229 | 2442.87 | 0.076906 | 3016.73 | 0.075008 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 600.238 | 540.107 | 728.907 | 155.763 | 969.577 | 490.257 | 1197.83 | 517.981 | 1444.63 | 244.239
48.8588 | 0.11156 | 190.363 | 0.094122 | 212.285 | 0.10957 | 201.528 | 0.14512 | 507.213 | 0.081826 | 535.891 | 0.08525 | 784.409 | 0.078382 | 845.502 | 0.086107 | 988.245 | 0.081417 | 1198.62 | 0.082483 | 1461.07 | 0.080527 | 1927.4 | 0.079407 | 2291.42 | 0.081907 | 2759.84 | 0.082318 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 725.574 | 235.444 | 968.467 | 520.659 | 1197.83 | 517.981 | 1450.44 | 350.424
45.2378 | 0.11775 | 176.431 | 0.09875 | 187.341 | 0.12183 | 186.034 | 0.15879 | 471.506 | 0.085763 | 492.715 | 0.090251 | 728.459 | 0.082648 | 779.717 | 0.092074 | 904.996 | 0.087496 | 1110.9 | 0.088198 | 1391.21 | 0.084149 | 1730.09 | 0.088022 | 2136.51 | 0.087934 | 2469.89 | 0.092906 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 726.822 | 326.016 | 968.467 | 520.659 | 1197.83 | 517.981 | 1441.32 | 444.752
41.5931 | 0.12604 | 160.763 | 0.10507 | 170.193 | 0.1337 | 171.903 | 0.17409 | 440.069 | 0.089711 | 447.167 | 0.097085 | 674.473 | 0.087321 | 708.345 | 0.10054 | 830.419 | 0.094405 | 1019.36 | 0.095544 | 1322.03 | 0.088198 | 1559.2 | 0.098454 | 1964.37 | 0.096601 | 2273.16 | 0.10268 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 472.603 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
37.635 | 0.13722 | 147.515 | 0.11201 | 151.856 | 0.1506 | 156.794 | 0.1959 | 398.589 | 0.096215 | 398.988 | 0.10687 | 634.559 | 0.091798 | 655.849 | 0.10794 | 753.652 | 0.10319 | 932.557 | 0.10423 | 1240.07 | 0.09384 | 1427.85 | 0.10848 | 1795.3 | 0.10697 | 2046.59 | 0.11693 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 728.072 | 574.917 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
34.7067 | 0.1485 | 130.442 | 0.12441 | 139.342 | 0.16593 | 145.755 | 0.21607 | 365.743 | 0.10319 | 353.871 | 0.11918 | 595.816 | 0.096505 | 606.031 | 0.11705 | 686.723 | 0.11359 | 856.566 | 0.11427 | 1180.78 | 0.098553 | 1308.88 | 0.12073 | 1670.58 | 0.11693 | 1879.81 | 0.13066 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
31.8149 | 0.16232 | 115.923 | 0.13888 | 123.462 | 0.19259 | 134.684 | 0.24168 | 330.607 | 0.11257 | 315.428 | 0.1345 | 551.66 | 0.10299 | 540.736 | 0.13263 | 641.578 | 0.12207 | 778.938 | 0.12705 | 1117.59 | 0.10433 | 1196.23 | 0.13531 | 1565.45 | 0.12692 | 1719.74 | 0.14776 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
28.8449 | 0.18156 | 103.33 | 0.15674 | 108.628 | 0.22828 | 123.956 | 0.27167 | 296.169 | 0.12504 | 283.137 | 0.1515 | 497.17 | 0.1137 | 494.195 | 0.14776 | 600.001 | 0.13171 | 712.608 | 0.14126 | 1049.35 | 0.11224 | 1093.27 | 0.15272 | 1425 | 0.14368 | 1578.02 | 0.1671 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
26.8948 | 0.19806 | 92.6597 | 0.17708 | 97.8987 | 0.2647 | 115.576 | 0.30205 | 268.253 | 0.1386 | 251.371 | 0.17479 | 460.324 | 0.12293 | 453.925 | 0.16379 | 547.811 | 0.14688 | 642.22 | 0.16151 | 991.214 | 0.11965 | 952.348 | 0.18467 | 1315.44 | 0.16039 | 1425 | 0.19492 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
24.6046 | 0.22243 | 83.6745 | 0.20066 | 88.1406 | 0.31063 | 106.797 | 0.34022 | 245.656 | 0.15302 | 230.426 | 0.1957 | 416.935 | 0.13708 | 421.126 | 0.18102 | 512.823 | 0.15943 | 583.434 | 0.18412 | 902.285 | 0.13397 | 867.774 | 0.21264 | 1211.88 | 0.17958 | 1301.05 | 0.22466 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
22.6222 | 0.25053 | 72.2357 | 0.24459 | 78.9594 | 0.36893 | 98.7838 | 0.38591 | 226.089 | 0.16861 | 211.438 | 0.22065 | 384.495 | 0.1506 | 390.697 | 0.20045 | 473.395 | 0.17743 | 533.752 | 0.20885 | 840.444 | 0.14614 | 791.501 | 0.24508 | 1097.65 | 0.2078 | 1198.62 | 0.25713 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
20.4081 | 0.29137 | 61.9876 | 0.30631 | 70.1008 | 0.44881 | 90.6435 | 0.44434 | 207.044 | 0.1884 | 195.572 | 0.2468 | 352.811 | 0.1671 | 354.579 | 0.22989 | 436.999 | 0.19806 | 485.38 | 0.24023 | 788.341 | 0.15895 | 729.188 | 0.27966 | 977.434 | 0.24879 | 1128.82 | 0.28446 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
18.8203 | 0.33215 | 55.2536 | 0.36635 | 62.9874 | 0.53732 | 83.5073 | 0.50958 | 188.657 | 0.21413 | 173.284 | 0.29548 | 324.061 | 0.18672 | 333.596 | 0.25204 | 404.613 | 0.22087 | 442.275 | 0.27716 | 725.551 | 0.17832 | 680.57 | 0.3125 | 886.19 | 0.29166 | 1065.21 | 0.31501 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
17.6712 | 0.37003 | 50.2462 | 0.42692 | 55.5306 | 0.67088 | 78.5656 | 0.56713 | 168.162 | 0.25204 | 153.382 | 0.35982 | 297.356 | 0.20989 | 310.732 | 0.28079 | 374.627 | 0.24804 | 389.916 | 0.33954 | 667.094 | 0.20106 | 641.578 | 0.34536 | 795.468 | 0.34848 | 1005.18 | 0.34988 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
16.6421 | 0.41141 | 46.2904 | 0.48862 | 50.1458 | 0.80641 | 74.8087 | 0.62116 | 150.194 | 0.29905 | 140.321 | 0.41596 | 273.672 | 0.23594 | 286.269 | 0.31849 | 351.051 | 0.27413 | 362.829 | 0.38475 | 577.629 | 0.24928 | 597.008 | 0.39017 | 727.731 | 0.40367 | 952.348 | 0.38745 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
15.6729 | 0.46248 | 43.2905 | 0.54872 | 45.2378 | 0.96738 | 69.7511 | 0.70317 | 138.786 | 0.33717 | 127.222 | 0.49354 | 245.901 | 0.27688 | 261.892 | 0.36782 | 323.737 | 0.31125 | 337.286 | 0.43424 | 504.179 | 0.3097 | 561.679 | 0.43164 | 686.037 | 0.44836 | 880.888 | 0.44702 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
14.8045 | 0.51832 | 40.8511 | 0.60643 | 42.0111 | 1.1139 | 65.8207 | 0.78258 | 130.182 | 0.373 | 119.933 | 0.54326 | 217.877 | 0.33315 | 241.515 | 0.42098 | 303.06 | 0.34675 | 320.516 | 0.47561 | 457.113 | 0.36416 | 531.09 | 0.47466 | 649.973 | 0.48862 | 832.082 | 0.4975 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
14.2098 | 0.56657 | 38.5492 | 0.66954 | 39.4855 | 1.2521 | 62.423 | 0.85971 | 123.215 | 0.4065 | 112.948 | 0.5986 | 197.933 | 0.38978 | 212.498 | 0.52144 | 274.22 | 0.40977 | 305.494 | 0.51832 | 409.498 | 0.44036 | 509.246 | 0.51316 | 616.422 | 0.5384 | 784.409 | 0.55981 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
13.5033 | 0.63625 | 35.8712 | 0.76173 | 37.3351 | 1.4005 | 58.7878 | 0.96835 | 116.971 | 0.44345 | 106.69 | 0.66222 | 175.727 | 0.47608 | 192.276 | 0.62116 | 253.644 | 0.469 | 294.103 | 0.55646 | 381.813 | 0.4985 | 489.768 | 0.55258 | 587.532 | 0.58851 | 740.208 | 0.62803 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
12.7934 | 0.72313 | 33.4795 | 0.86143 | 35.979 | 1.5096 | 56.1448 | 1.0638 | 111.044 | 0.48522 | 98.3895 | 0.76479 | 157.108 | 0.58033 | 175.551 | 0.72821 | 231.119 | 0.55092 | 278.086 | 0.61498 | 361.38 | 0.54763 | 470.564 | 0.59324 | 551.66 | 0.66288 | 701.998 | 0.69966 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
11.9763 | 0.8503 | 31.6562 | 0.95584 | 34.4991 | 1.6452 | 53.7817 | 1.1616 | 104.682 | 0.53517 | 92.7524 | 0.85457 | 143.299 | 0.68102 | 161.569 | 0.84437 | 211.438 | 0.64265 | 267.182 | 0.66421 | 343.756 | 0.5992 | 440.509 | 0.6729 | 521.094 | 0.73996 | 669.768 | 0.77093 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
11.4036 | 0.97223 | 29.664 | 1.0777 | 33.246 | 1.7768 | 51.6729 | 1.2596 | 99.5772 | 0.58382 | 85.9644 | 0.98299 | 129.144 | 0.82517 | 150.796 | 0.95776 | 188.657 | 0.79124 | 257.735 | 0.71237 | 330.277 | 0.64651 | 417.77 | 0.74814 | 490.258 | 0.83681 | 626.364 | 0.88855 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
10.9128 | 1.1061 | 27.2467 | 1.2596 | 31.9744 | 1.9403 | 49.6965 | 1.3659 | 93.7783 | 0.64975 | 82.0176 | 1.0799 | 120.173 | 0.94444 | 140.883 | 1.0962 | 173.457 | 0.93318 | 246.887 | 0.77402 | 314.169 | 0.71095 | 389.526 | 0.86316 | 461.246 | 0.94823 | 597.606 | 0.98397 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
10.4744 | 1.2609 | 25.4047 | 1.4388 | 30.8746 | 2.0935 | 47.6048 | 1.4961 | 86.309 | 0.75415 | 77.5508 | 1.2042 | 112.835 | 1.067 | 131.358 | 1.2534 | 163.847 | 1.0438 | 234.611 | 0.85628 | 297.952 | 0.78572 | 367.576 | 0.9732 | 439.19 | 1.049 | 561.679 | 1.133 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
10.1141 | 1.4132 | 23.9013 | 1.6142 | 29.7234 | 2.277 | 45.1023 | 1.6684 | 79.9126 | 0.86748 | 73.3274 | 1.3469 | 106.264 | 1.1946 | 123.092 | 1.4274 | 153.843 | 1.1875 | 221.391 | 0.96545 | 283.988 | 0.86229 | 347.558 | 1.0951 | 424.084 | 1.1341 | 530.559 | 1.2902 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
9.8054 | 1.5759 | 22.6902 | 1.7822 | 28.7873 | 2.4567 | 43.2905 | 1.8328 | 74.5846 | 0.9889 | 70.2411 | 1.4767 | 101.588 | 1.3111 | 116.855 | 1.5902 | 145.319 | 1.3389 | 208.29 | 1.0984 | 268.79 | 0.96256 | 327.318 | 1.2434 | 407.863 | 1.2434 | 504.179 | 1.4577 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
9.4021 | 1.831 | 21.6268 | 1.9637 | 27.6862 | 2.6854 | 41.2204 | 2.0357 | 69.8908 | 1.1206 | 66.7486 | 1.6484 | 96.5377 | 1.4577 | 109.939 | 1.8218 | 136.993 | 1.5248 | 198.528 | 1.2175 | 256.706 | 1.0564 | 310.111 | 1.4033 | 395.018 | 1.3296 | 485.865 | 1.5902 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
9.1334 | 2.0459 | 20.7788 | 2.1337 | 26.5475 | 2.9738 | 39.3279 | 2.2633 | 65.5579 | 1.2723 | 63.3664 | 1.8531 | 92.9381 | 1.5759 | 104.682 | 2.0255 | 130.703 | 1.6936 | 190.363 | 1.3309 | 244.675 | 1.1651 | 296.466 | 1.5509 | 382.195 | 1.4331 | 472.45 | 1.7106 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
8.8901 | 2.3068 | 19.8844 | 2.344 | 25.532 | 3.2571 | 37.7858 | 2.4765 | 62.1738 | 1.416 | 60.4571 | 2.0582 | 89.1155 | 1.7312 | 98.9816 | 2.3068 | 124.453 | 1.8981 | 183.081 | 1.4635 | 232.742 | 1.2954 | 282.289 | 1.7539 | 367.209 | 1.5791 | 456.2 | 1.8792 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
8.7141 | 2.5596 | 19.1429 | 2.5545 | 24.6292 | 3.571 | 35.9071 | 2.7866 | 58.8466 | 1.587 | 57.7391 | 2.3045 | 85.5357 | 1.8943 | 93.3106 | 2.6454 | 118.739 | 2.1337 | 176.255 | 1.5965 | 223.616 | 1.426 | 270.678 | 1.9422 | 354.579 | 1.7261 | 439.629 | 2.0706 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
8.5074 | 2.9237 | 18.3739 | 2.809 | 23.8536 | 3.8917 | 34.6374 | 3.0308 | 55.8089 | 1.7733 | 55.1984 | 2.5776 | 81.2827 | 2.1315 | 89.8313 | 2.9033 | 113.061 | 2.4178 | 170.875 | 1.7278 | 212.71 | 1.5981 | 263.204 | 2.0914 | 342.041 | 1.8848 | 421.126 | 2.3276 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
8.3223 | 3.3196 | 17.742 | 3.0582 | 23.1717 | 4.2032 | 33.513 | 3.28 | 53.1402 | 1.9716 | 52.7695 | 2.8946 | 77.4733 | 2.3937 | 85.1091 | 3.3262 | 108.086 | 2.7097 | 165.163 | 1.8773 | 204.574 | 1.7539 | 254.66 | 2.2861 | 330.607 | 2.0562 | 407.048 | 2.5596 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
8.1331 | 3.88 | 17.166 | 3.313 | 22.0858 | 4.8107 | 32.5551 | 3.5178 | 50.4475 | 2.203 | 50.8527 | 3.215 | 73.8425 | 2.6801 | 80.7158 | 3.8414 | 103.641 | 3.043 | 160.442 | 2.0114 | 196.749 | 1.9306 | 246.887 | 2.5089 | 318.28 | 2.2815 | 393.835 | 2.8203 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
8.012 | 4.3835 | 16.5425 | 3.6359 | 21.3902 | 5.2954 | 31.4668 | 3.8261 | 47.9392 | 2.474 | 48.6637 | 3.6541 | 71.018 | 2.9619 | 76.3199 | 4.49 | 99.7766 | 3.4002 | 155.233 | 2.2052 | 189.792 | 2.1188 | 239.83 | 2.7287 | 304.884 | 2.5647 | 379.909 | 3.1294 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.869 | 5.0372 | 15.9098 | 4.0222 | 20.7788 | 5.7941 | 30.3845 | 4.2116 | 45.3284 | 2.8203 | 46.99 | 4.0912 | 68.3016 | 3.2833 | 73.6213 | 5.012 | 96.1523 | 3.7994 | 150.345 | 2.4009 | 181.623 | 2.3841 | 231.581 | 3.0127 | 295.873 | 2.8203 | 368.681 | 3.4378 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.7596 | 5.7999 | 15.3319 | 4.4497 | 20.2455 | 6.2893 | 29.3982 | 4.6082 | 43.5511 | 3.1357 | 45.3738 | 4.599 | 65.1657 | 3.7428 | 71.018 | 5.6173 | 93.2173 | 4.2369 | 144.739 | 2.6614 | 173.457 | 2.7097 | 224.512 | 3.313 | 284.272 | 3.1767 | 359.578 | 3.7541 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.6441 | 6.6715 | 14.9085 | 4.8203 | 19.7062 | 6.8953 | 28.4439 | 5.0827 | 41.8016 | 3.4689 | 43.7694 | 5.1958 | 62.9244 | 4.1158 | 68.5069 | 6.3398 | 90.5529 | 4.7249 | 139.621 | 2.9708 | 166.157 | 3.0521 | 216.357 | 3.6761 | 277.531 | 3.4793 | 349.999 | 4.1406 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.5378 | 7.5674 | 14.4535 | 5.3113 | 19.2774 | 7.4696 | 27.274 | 5.7136 | 40.1224 | 3.8568 | 42.1373 | 5.923 | 60.9427 | 4.5305 | 66.3493 | 7.1338 | 88.1406 | 5.2954 | 134.28 | 3.3429 | 160.121 | 3.4275 | 209.543 | 4.0871 | 268.522 | 3.8956 | 343.412 | 4.4765 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.4479 | 8.7045 | 14.0403 | 5.8524 | 18.8203 | 8.2058 | 26.5475 | 6.208 | 38.5106 | 4.2967 | 40.7695 | 6.7116 | 58.7878 | 5.0725 | 64.5173 | 7.9952 | 85.4502 | 6.0427 | 128.757 | 3.8146 | 154.768 | 3.8184 | 204.984 | 4.4364 | 263.995 | 4.2454 | 336.276 | 4.8981 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.3738 | 10.174 | 13.6526 | 6.5133 | 18.3923 | 9.0056 | 25.8144 | 6.7656 | 37.0376 | 4.7963 | 39.525 | 7.5825 | 57.2217 | 5.5725 | 62.8615 | 8.9517 | 83.3404 | 6.8472 | 125.202 | 4.2369 | 150.495 | 4.1697 | 199.923 | 4.8639 | 257.735 | 4.706 | 329.287 | 5.3701 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.3078 | 12.2049 | 13.4091 | 7.0206 | 18.0823 | 9.8143 | 25.1771 | 7.3144 | 35.9071 | 5.227 | 38.5106 | 8.5066 | 55.6418 | 6.1647 | 60.9427 | 10.2866 | 80.7965 | 8.1812 | 122.355 | 4.6267 | 147.515 | 4.4944 | 195.572 | 5.306 | 252.884 | 5.1699 | 322.122 | 5.9586 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.2423 | 14.6559 | 13.078 | 7.7822 | 17.7597 | 10.6957 | 24.7032 | 7.8762 | 35.0556 | 5.5892 | 37.5222 | 9.572 | 54.1595 | 6.7723 | 59.557 | 11.7264 | 78.6442 | 9.707 | 119.693 | 5.1544 | 144.739 | 4.8348 | 191.126 | 5.9053 | 248.373 | 5.7537 | 316.692 | 6.5198 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.1918 | 17.5112 | 12.7296 | 8.6698 | 17.4953 | 11.6329 | 24.2383 | 8.4557 | 34.19 | 6.0245 | 36.6691 | 10.6423 | 52.8223 | 7.4622 | 58.6703 | 13.2083 | 76.5492 | 11.7499 | 117.206 | 5.7825 | 142.299 | 5.2375 | 187.341 | 6.4873 | 243.211 | 6.5003 | 311.043 | 7.1696 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.1416 | 21.2391 | 12.4526 | 9.6682 | 17.2866 | 12.7923 | 23.8536 | 9.1692 | 33.4126 | 6.5133 | 36.051 | 11.8324 | 51.6213 | 8.2305 | 57.5661 | 15.2998 | 74.6592 | 14.2227 | 114.312 | 6.5853 | 139.9 | 5.6908 | 183.448 | 7.2344 | 237.206 | 7.4547 | 304.884 | 7.9236 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.1416 | 24.8248 | 12.1939 | 10.8791 | 17.0634 | 14.1943 | 23.4749 | 9.9926 | 32.751 | 6.9786 | 35.5143 | 13.0768 | 50.7004 | 9.0236 | 56.5392 | 18.135 | 72.9616 | 17.7759 | 112.61 | 7.3584 | 137.542 | 6.2454 | 179.995 | 8.0353 | 232.742 | 8.422 | 297.952 | 9.1143 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.1202 | 30.2606 | 11.9644 | 12.6144 | 16.8767 | 15.7186 | 23.0792 | 10.9445 | 31.9744 | 7.5977 | 35.0205 | 15.0269 | 49.8458 | 9.9527 | 55.6418 | 22.1059 | 72.0193 | 20.0223 | 110.049 | 8.5835 | 135.088 | 6.9646 | 176.431 | 8.9966 | 228.362 | 9.5529 | 292.344 | 10.225 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.106 | 36.9234 | 11.8335 | 13.9411 | 16.6921 | 17.5814 | 22.804 | 11.8442 | 31.404 | 8.1731 | 34.4991 | 17.9366 | 49.202 | 10.8573 | 54.978 | 26.5717 | 71.374 | 22.575 | 107.978 | 9.8932 | 132.546 | 7.7822 | 173.978 | 10.0126 | 224.064 | 11.0545 | 286.842 | 11.6213 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0989 | 50.0413 | 11.6923 | 15.6089 | 16.5425 | 19.7636 | 22.5319 | 12.9726 | 30.7821 | 8.8273 | 34.1559 | 20.4267 | 48.276 | 12.3646 | 54.5945 | 32.2283 | 70.4522 | 26.5451 | 105.84 | 11.4598 | 130.573 | 8.6525 | 170.704 | 11.2328 | 219.847 | 12.7923 | 281.443 | 13.4213 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0705 | 63.8699 | 11.5992 | 17.4937 | 16.3943 | 22.2612 | 22.2854 | 14.0812 | 30.2028 | 9.707 | 33.816 | 24.3576 | 47.32 | 14.337 | 54.5945 | 39.7992 | 69.8209 | 30.4731 | 103.952 | 13.4482 | 128.5 | 9.6973 | 167.994 | 12.5892 | 215.494 | 15.2083 | 276.699 | 15.3458 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0635 | 90.0936 | 11.5182 | 19.7834 | 16.2637 | 25.2757 | 22.13 | 15.4691 | 29.7531 | 10.4004 | 33.6137 | 28.6126 | 46.6155 | 16.5741 | 54.5945 | 49.0504 | 69.1954 | 35.3694 | 101.996 | 16.2948 | 126.587 | 10.8791 | 165.825 | 14.039 | 210.804 | 18.2077 | 272.307 | 17.4239 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0635 | 116.03 | 11.4608 | 22.1059 | 16.1502 | 28.6698 | 21.9976 | 17.0107 | 29.2809 | 11.4483 | 33.5466 | 33.7455 | 45.8756 | 19.7044 | 54.5945 | 65.095 | 68.5069 | 43.5038 | 99.4777 | 21.2604 | 124.952 | 12.0835 | 163.519 | 15.5156 | 206.424 | 22.8247 | 267.985 | 20.0623 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 163.016 | 11.3809 | 25.5298 | 16.0536 | 32.0676 | 21.8879 | 18.706 | 28.9895 | 12.303 | 33.4795 | 39.2459 | 45.4646 | 23.3558 | 54.5945 | 85.443 | 67.8931 | 54.2633 | 98.0947 | 25.5298 | 123.215 | 13.997 | 161.407 | 17.4937 | 202.741 | 28.5554 | 262.416 | 24.2361 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 213.119 | 11.3581 | 29.9595 | 15.9416 | 37.22 | 21.8879 | 599.954 | 28.7298 | 13.3277 | 33.3125 | 47.1271 | 45.0122 | 27.4632 | 54.5945 | 123.575 | 67.3521 | 67.7516 | 97.0216 | 30.0495 | 121.38 | 16.0522 | 159.482 | 19.7242 | 199.125 | 34.9126 | 258.768 | 27.7947 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 316.667 | 11.3468 | 34.5997 | 15.8939 | 42.9419 | 21.8879 | 599.954 | 28.3587 | 15.2235 | 33.1796 | 57.0454 | 44.6089 | 32.8465 | 54.5945 | 170.008 | 66.8823 | 88.398 | 95.7685 | 36.8128 | 119.933 | 18.781 | 157.58 | 22.3952 | 195.768 | 45.9635 | 255.17 | 32.1318 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 409.875 | 11.3468 | 149.134 | 15.8621 | 49.3949 | 21.8879 | 599.954 | 28.302 | 17.4588 | 33.0802 | 69.1203 | 44.3864 | 39.0111 | 54.5945 | 228.115 | 66.3493 | 117.196 | 95.0054 | 43.0709 | 118.384 | 21.9737 | 155.856 | 25.9935 | 192.661 | 59.2549 | 251.623 | 37.1085 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 484.372 | 11.3354 | 202.32 | 15.8463 | 69.0512 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9811 | 84.5928 | 44.1651 | 49.3456 | 54.5945 | 306.081 | 66.1506 | 161.233 | 93.8721 | 52.8178 | 117.206 | 25.4024 | 154.151 | 29.249 | 189.792 | 75.6297 | 248.125 | 42.8989 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 543.404 | 11.3354 | 599.954 | 15.8463 | 504.139 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 98.0865 | 44.0768 | 60.2106 | 54.54 | 429.599 | 65.8865 | 210.366 | 93.0311 | 67.2118 | 116.155 | 29.6317 | 152.312 | 34.3584 | 187.341 | 94.9974 | 245.165 | 48.4653 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 44.0768 | 76.696 | 54.54 | 520.533 | 65.8865 | 270.657 | 92.0134 | 85.9572 | 113.969 | 42.8132 | 150.495 | 40.8067 | 184.737 | 124.318 | 242.24 | 56.3086 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 44.0328 | 103.839 | 54.54 | 577.584 | 65.8865 | 332.57 | 91.3715 | 104.988 | 112.497 | 61.2429 | 148.551 | 53.5624 | 182.716 | 159.309 | 239.112 | 64.5118 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.9888 | 130.823 | 54.54 | 599.954 | 65.8865 | 414.823 | 90.8249 | 126.703 | 111.267 | 87.0819 | 147.368 | 64.1259 | 181.26 | 207.027 | 233.441 | 88.8411 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.6819 | 305.47 | 54.54 | 599.954 | 65.8865 | 491.201 | 90.3719 | 155.066 | 110.27 | 127.593 | 146.193 | 76.4662 | 179.995 | 258.747 | 228.133 | 122.223 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.464 | 473.832 | 54.54 | 599.954 | 65.8865 | 566.147 | 89.3833 | 255.66 | 109.61 | 223.598 | 144.884 | 98.0865 | 178.74 | 325.985 | 223.616 | 178.19 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 88.3171 | 422.78 | 108.954 | 347.878 | 142.869 | 141.012 | 176.431 | 499.123 | 220.067 | 251.602 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 298.379 | 601.196 | 357.597 | 599.476 | 421.506 | 599.82 | 482.254 | 597.076 | 599.894 | 600.164 | 727.238 | 601.885 | 968.467 | 520.659 | 1197.83 | 517.981 | 1437.2 | 523.651